| 1) Inspector Name: RON ANTHONY Inspector Code: 875 |  | 2) Inspection Date: JULY 04, 2025 |  |  |  |  | 3) Project Name (if any): TABRIZ PETROCHEMICAL CO. |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 4) Scope of Inspection Required: Inspection Notification No.: IDR-TPC-IN-HEU-9008-003 |  |  |  |  |  |  |  |  |  |
| 5) Inspection Address & Contact Info: Company Name: AUTO CONTROL PROCESS Address: HAMRIYAH FREEZONE Contact Name: ATEEQ Phone Number / Mobile Number: +971529952816 E-mail Address: ASGARI@HAMTAENERGY.COM |  |  |  |  |  |  |  |  |  |
| 6) Inspection Place: Manufacturer Supplier Warehouse Port Customs Others Specify: |  |  |  |  |  |  |  |  |  |
| 7) Client/Buyer: TABRIZ PETROCHEMICAL CO. TEHRAN IRAN |  |  |  |  | 8) Vendor/Sub-Vendor: HAMTA ENERGY PAYA DUBAI UAE |  |  |  |  |
| 9) Goods as Per Purchasing Documents: FLARE GAS ULTRA SONIC FLOWMETERS |  |  |  |  |  |  |  |  |  |
| 10) Quality Inspection : |  |  |  |  |  |  |  |  |  |
| Visual | Dimensional |  | Test |  |  |  |  | Doc’s Review |  |
| %100 Spot Check | %100 Spot Check |  | %100 Spot Check |  |  |  |  |  |  |
| Random No. of Items Checked: | Random No. of Items Checked: |  | Random No. of Items Checked: |  |  |  |  |  |  |
| 11) Quantity Inspection : |  |  |  |  |  |  |  |  |  |
| Tally | Weight |  |  | Volume |  | Length |  |  | Others (Specify) |
| %100 Spot Check | %100 Spot Check |  |  | %100 Spot Check |  | %100 Spot Check |  |  |  |
| Random No. of Items Checked: | Random No. of Items Checked: |  |  | Random No. of Items Checked: |  | Random No. of Items Checked: |  |  |  |
| 12) Brief Description of Packing: Kind of Packing: FINAL PACKING IS NOT PERFORM YET Total Number of Packages: NOT AVAILABLE YET Total Net weight: FINAL PACKING LIST IS REQUIRED Total Gross weight: FINAL PACKING LIST IS REQUIRED |  |  |  | 13) Shipping Mark (Please specify details in item 22): FINAL SHIPPING MARKING WILL BE ARRANGE ON THE PACKAGE AFTER FINAL PACKING |  |  |  |  |  |
| 14) Means of Transport: Truck Vessel Air Rail Combined Shipment From: NO INFO Via: NO INFO To: NO INFO |  |  |  |  |  |  |  |  |  |
| 15) Conclusion (Explain Briefly): Stage (Inspection of the goods in this visit is satisfactory. Goods are released for further inspection) Satisfactory (Inspection of the goods is satisfactory. Goods are released for shipment) Non-Conformity (Discrepancies observed. Goods could not be released) Abortive (Due to missing goods and/or documents, inspection could not be carried out) Inspection completed? No Yes When No, Specify next insp. scope: |  |  |  |  |  |  |  |  |  |
| 16) Documents Used for Inspection: L/C No.:; No. of L/C Amendments:; P/I No.:. Tech. Spec. No.:; P/O No. / MR No.:; ITP No.:. Drawing No.:; Procedure No.:; Data Sheet No.:. Others:. Necessary Documents for Issuance of COI Has Been Collected: Yes No. |
| 17) Goods Inspected In Details: SUPPLIED COMMODITIES AS PER PACKING LIST. ITEM NO.; ITEM DESCRIPTION; QTY. 1.; FLARE GAS ULTRA SONIC FLOW METER, TAG NO. 16FT-00709; 2 SETS INCLUDING COMMISSIONING SPARE PARTS, 2 YEARS SPARE PARTS AND OTHER ACCESSORIES AS PER PACKING LIST ATTACHED.. 2.; FLARE GAS ULTRA SONIC FLOW METER, TAG NO. 16FT-00711. |
| 18) Order Completed? Yes No Comments (If any): |  |  |  |  |  |  |  |  |  |

| 19) Quality Inspection (Detailed description of quality inspection and assessment of quality control): |  |  |  |
| --- | --- | --- | --- |
| THE UNDERSIGNED INSPECTOR CARRIED OUT THE INSPECTION AT SUPPLIER WAREHOUSE LOCATED IN HAMRIYAH FREEZONE SHARJAH UAE, CONDUCTED ON THE DATE OF JULY 04, 2025 WITH REFERENCE TO THE INSPECTION NOTIFICATION NO.IDR-TPC-IN-HEU-9008-003. INSPECTION DETAILS AND RESULTS: (PROVIDED DETAILS, FINDINGS AND CONCLUSIONS AS PER ITP). SCOPE AND ACTIVITIES PERFORMED: - QUANTITY (GENERAL CONTROL OF ITEMS QUANTITIES). SUPPLIED COMMODITIES AS PER PACKING LIST. ITEM NO.; ITEM DESCRIPTION; QTY. 1.; FLARE GAS ULTRA SONIC FLOW METER, TAG NO. 16FT-00709; 2 SETS INCLUDING COMMISSIONING SPARE PARTS, 2 YEARS SPARE PARTS AND OTHER ACCESSORIES AS PER PACKING LIST ATTACHED.. 2.; FLARE GAS ULTRA SONIC FLOW METER, TAG NO. 16FT-00711. - TOTAL OF 2 SETS. OF INTERFACE UNIT WITH A TAG NO. OF 16FT-00709 AND 15FT-00711, 2 SETS OF SLAVE/MASTER SENSORS AND 31 PCS OF RELATED COMPONENTS AND ACCESSORIES INCLUDING (50 MTRS OF CONNECTION CABLES) HAVE BEEN INSPECTED AT FOUND AVAILABLE AT SUPPLIER WAREHOUSE, THE QUANTITY SUPPLIED WAS FOUND IN LINE AS PER SUBMITTED PACKING LIST. A DETAILED AND ITEMIZED LIST COVERING ALL THE ITEMS OF THE PACKING LIST HAVE BEEN ATTACHED AS WELL ON THE IR FOR REFERENCE. - QUALITY(VISUAL INSPECTION) - 100% OF THE SUPPLIED COMMODITIES WERE UNPACKED FOR CONTROLLING THE QUALITY WERE CARRIED OUT WITH SATISFACTORY RESULTS, THE SUPPLIED INTERFACE UNITS, MASTER SENSOR AND SLAVE SENSORS INCLUDING RELATED COMPONENTS AND ACCESSORIES WERE FOUND IN BRAND NEW CONDITION AND NO OBSERVED DAMAGES AT THE TIME OF INSPECTION. DESCRIPTIONS OF THE ITEMIZED LIST PROVIDED AND PACKING LIST DESCRIPTION WAS CONFORMING TO THE INSPECTED COMMODITIES EXCEPT ITEM NO. 7 OF ATTACHED PACKING LIST. - CONTROL OF THE LABEL OF THE PRODUCT - MANUFACTURER MILL MARKING AND LABELS ARE PRESENT ON THE INSPECTED COMMODITIES, TAG NOS. ARE TRACEABLE AS WELL, BASIC SPECIFICATION ARE TRACEABLE AND QUANTITY SPECIFIED IN THE MARKING INCLUDING SIZING AND MODEL DESCRIPTION. - DOCUMENT REVIEW, DIMENSION TEST AS PER SUBMITTED GAD FOR RELATED PARTS AND COMPONENTS, CALIBRATION REVIEW OF FLOW METERS, ATEX/IP CERTIFICATES, NAMEPLATE AND TAGGING. - VERIFICATION OF TAG NUMBERS AND NAME PLATE CARRIED OUT FOR 16FT-00709 AND 16FT-0071, DIMENSION TEST CARRIED OUT WITH SATISFACTORY RESULTS. REVIEW OF THE CALIBRATION AND ATEX/IP CERTIFICATES HAVE BEEN CARRIED OUT WITH ACCEPTABLE RESULTS. OVER ALL DOCUMENT VERIFICATION AND SUBMITTAL OF ORIGINAL DOCUMENTS WERE CONDUCTED AT THE TIME OF INSPECTION. COPY OF ORIGINAL DOCUMENTS HAVE BEEN ATTACHED ON THE IR. - PACKAGING QUALITY CONTROL - FINAL PACKING OF THE INSPECTED COMMODITIES ARE NOT PREPARED YET. - SHIPPING MARKING - FINAL SHIPPING MARKING WILL BE ARRANGED AFTER FINAL PACKING OF THE GOODS. |
| 19-1) Marking on Goods as per specific requirements: |  |  |
| AS PER PHOTOS |  |  |
| 19-2) Instruments Used (Meter ,Slide Caliper ,Gauge,…) and Calibration Code/Date: |  |  |
| NOT APPLICABLE |  |  |
| 20) Quantity Inspection (Detailed description of inspected quantity and assessment of quantity control): |  |  |  |
| ITEM NO.; ITEM CODE / TAG NO.; DESCRIPTION; QUANTITY; UNIT. 1; 16FT-00709; FLARE GAS ULTRASONIC FLOWMETER INCLUDING SLAVE SENSOR, MASTER SENSOR AND SUNSHADE, INTERFACE UNIT, CONNECTION CABLE BETWEEN SENSORS AND SUNSHADE; 1; NO.. 2; 16FT-00711; FLARE GAS ULTRASONIC FLOWMETER INCLUDING SLAVE SENSOR, MASTER SENSOR AND SUNSHADE, INTERFACE UNIT, CONNECTION CABLE BETWEEN SENSORS AND SUNSHADE; 1; NO.. 3; COMMISSIONING SPARE PART; ASSEMBLY KIT ANSI300 2Z SS ET INCLUDING WELD ON NOZZLES MATERIAL LTCS, NOZZLE INSTALLATIONS TOOL 1 PATH AND NOZZLE ISOLATION SET 2/DN50; 2; NO.. 4; COMMISSIONING SPARE PART; FUSE KIT POWER SUPPLY - 3A15 (=3.15 AMPER) 250V D5*20 FOR ALL INTERFACE UNITS WITH 110 VAC POWER SUPPLY; 1; NO.. 5; 2-YEARS SPARE PART; REPLACEMENT COVER FOR ALUMINUM EXD M20 HOUSING CONTENTS: COVER, COVER LOCK, COVER INSULATION, O-RING, SPRING WASHER, SCREWS, ASSEMBLY PASTE, SEALING PLUGS; 1; NO.. 6; FOR TAGS 16FT-00709 & 16FT-00711; BALL VALVE 2", CL300#, BODY AND BALL MATERIAL CS; 4; NO.. 7; FOR TAGS 16FT-00709 & 16FT-00711; CONNECTION CABLE BETWEEN MASTER SENSOR AND INTERFACE UNIT (2X2X0.5 MM2, LENGTH 25 M); 2 X 25; MTR. 8; FOR TAGS 16FT-00709 & 16FT-00711; CABLE GLAND M20*1,5 D12,5-20,9 EX MS FOR ARMORED CABLE TYPES, MATERIAL BRASS NICKEL-PLATED; 4; NO.. REFERENCE. PACKING LIST NO. HDPE-16-9008-HEU-002 ITEMIZED QUANTITY AS PER PACKING LIST TOTAL: 35 NOS. + 2 SETS (50MTRS OF CABLE) |
| 21) Packing Inspection (Detailed description of packing and suitability with the means of transport): |  |  |  |
| FINAL PACKING OF THE GOODS WERE NOT PERFORMED YET. |  |  |  |
| 22) Shipping Mark Inspection (Detailed description of marking on the packages): |  |  |  |
| SHIPPING MARKING WILL BE ARRACHED ON THE PACKAGE AFTER FINAL PACKING. |  |  |  |
| 23) Loading / Stuffing Inspection: |  |  |  |
| Weather condition: N/A |  |  |  |
| Start of loading time: N/A | Finish of loading time: N/A |  |  |
| No. of container(s): N/A |  |  |  |
| Seal No.(s): N/A |  |  |  |
| Comments on Loading / Stuffing Inspection: |  |  |  |
| N/A |  |  |  |
| 24) Discrepancies (Detailed description of discrepancies observed during inspection): |  |  |  |
| - Discrepancies which found during inspection and already obviated : |  |  |  |
| - THE DESCRIPTION OF THE SUPPLIED CABLE FOR ITEM NO. 7 OF THE PACKING LIST IS TYPE: Li2YCYv(TP), WHILE THE ACTUAL SUPPLIED MATERIAL WAS RE-2Y(ST)Yv PiMF. CLIENT CONFIRMATION IS REQUIRED. - FINAL PACKING OF THE GOODS WERE NOT PERFORMED AFTER INSPECTION. - FINAL SHIPPING MARKING WILL BE ADDED AFTER FINAL PACKING OF THE GOODS. - ITEM NO. 6 OF ATTACHED PL, 4 NOS. OF 2” BALL VALVE. NO CERTIFICATES, TEST REPORTS AND DRAWINGS SUBMITTED FOR THIS ITEM. |  |  |  |
| - Discrepancies which are still remained : |  |  |  |
| - THE DESCRIPTION OF THE SUPPLIED CABLE FOR ITEM NO. 7 OF THE PACKING LIST IS TYPE: Li2YCYv(TP), WHILE THE ACTUAL SUPPLIED MATERIAL WAS RE-2Y(ST)Yv PiMF. CLIENT CONFIRMATION IS REQUIRED. - FINAL PACKING OF THE GOODS WERE NOT PERFORMED AFTER INSPECTION. - FINAL SHIPPING MARKING WILL BE ADDED AFTER FINAL PACKING OF THE GOODS. - ITEM NO. 6 OF ATTACHED PL, 4 NOS. OF 2” BALL VALVE. NO CERTIFICATES, TEST REPORTS AND DRAWINGS SUBMITTED FOR THIS ITEM. |  |  |  |
| 25) Attachments (List of attached documents): |  |  |  |
| AS ATTACHED |  |  |  |
| 26) Comments (Regarding inspection – if any): |  |  |  |
| NONE |  |  |  |
| PHOTOS |  |  |  |