| 1) Inspector Name: Ali Malek Inspector Code: 693 |  | 2) Inspection Date: 2025-08-04 to 06 (3 days) |  |  |  | 3) Project Name (if any): |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 4) Scope of Inspection Required: Performance Test IDR IN-MA-TPC-KPS-4001-0009 |  |  |  |  |  |  |  |
| 5) Inspection Address & Contact Info: KSB SE & Co. KGaA Bahnhofplatz 1 91257 Pegnitz / Germany Mr. Andreas Kreuzer, Andreas.Kreuzer@KSB.com, +49 9241 711244 |  |  |  |  |  |  |  |
| 6) Inspection Place: Manufacturer Supplier Warehouse Port Customs Others Specify: |  |  |  |  |  |  |  |
| 7) Client/Buyer: TPC / EIED |  |  |  | 8) Vendor/Sub-Vendor: Tianjin KPT M&E Equipment Enginnering Co. Ltd |  |  |  |
| 9) Goods as Per Purchasing Documents: 8 x centrifugal pumps (suspension pumps) with tag numbers 16-P-121 A/B, 16-P-122 A/B, 16-P-123 A/B and 16-P-131 A/B |  |  |  |  |  |  |  |
| 10) Quality Inspection : |  |  |  |  |  |  |  |
| Visual | Dimensional check |  | Test |  | Doc’s Review |  |  |
| %100 Spot Check | %100 Spot Check |  | %100 Spot Check |  |  |  |  |
| Random No. of Items Checked: 8 Items | Random No. of Items Checked: 0 |  | Random No. of Items Checked: 8 |  |  |  |  |
| 11) Quantity Inspection : |  |  |  |  |  |  |  |
| Tally | Weight |  | Volume |  | Length |  | Others (Specify) |
| %100 Spot Check | %100 Spot Check |  | %100 Spot Check |  | %100 Spot Check |  |  |
| Random No. of Items Checked: 8 items | Random No. of Items Checked: |  | Random No. of Items Checked: |  | Random No. of Items Checked: |  |  |
| 12) Brief Description of Packing: Kind of Packing: Total Number of Packages: Total Net weight: Total Gross weight: |  |  | 13) Shipping Mark (Please specify details in item 22): |  |  |  |  |
| 14) Means of Transport: Truck Vessel Air Rail Combined Shipment From: Via: To: |  |  |  |  |  |  |  |
| 15) Conclusion (Explain Briefly): Stage (Inspection of the goods in this visit is satisfactory. Goods are released for further inspection) Satisfactory (Inspection of the goods is satisfactory. Goods are released for shipment) Non-Conformity (Discrepancies observed. Goods could not be released) Abortive (Due to missing goods and/or documents, inspection could not be carried out) Inspection completed? No Yes When No, Specify next insp. scope: |  |  |  |  |  |  |  |
| 16) Documents Used for Inspection: L/C No.:; No. of L/C Amendments:; P/I No.:. Tech. Spec. No.:; PO No.: HDPE-16-DD-00-MA-PO-4001. Drawing No.:. Others:. Necessary Documents for Issuance of COI Has Been Collected: Yes No. |
| 17) Goods Inspected In Details: 8 x centrifugal pumps (suspension pumps) with tag numbers 16-P-121 A/B, 16-P-122 A/B, 16-P-123 A/B and 16-P-131 A/B - Test result for pumps with tag numbers 16-P-121 A/B, 16-P-122 A, 16-P-123 A/B and 16-P-131 A/B was acceptable - Pump 16-P-122 B was made some unusual noises during the starting of mechanical run. Mechanical run was immediately stopped and pump was opened. As visible on attached photos, bearing was damaged in the pump. KSB is going to check all other pump pieces regarding damages and after installing new bearings, test must be repeated. |  |  |  |  |  |  |  |
| 18) Order Completed? Yes No Comments (If any): |  |  |  |  |  |  |  |

| 19) Quality Inspection (Detailed description of quality inspection and assessment of quality control): |  |  |
| --- | --- | --- |
| An inspection visit was conducted to KSB SE Co. KGaA in Pegnitz / Germany on 2025-07-04/05/06 to witness the performance test and mechanical running test on 8 KWPO centrifugal pumps with tag numbers 16-P-121 A/B, 16-P-122 A/B, 16-P-123 A/B and 16-P-131 A/B as defined in IDR IN-MA-TPC-KPS-4001-0009. Tests were performed acc. to KSB performance test procedure AN1897/70-09 Rev. 00 based on KSB Germany ITP. ITP Hydraulic performance test: Pumps were connected via shop coupling to the shop motor. Flow meter at suction side, head measuring facility at discharge side, torque and rotation speed facility on shaft. Motor was started and run to the rated flow and rated head with constant speed. At least six points were run for performance test (shut off, min. flow, 95%-99% of rated flow, 100%-105% of rated flow, best efficiency point and max. flow). Performance test is acc. to API 610 and procedure AN 1897/70-05 but mechanical run was performed acc. to AN 1897/70-09 with limits for bearing vibration and temperature from ITP. Following pumps were tested with following results. Only results of pump A will be discussed here as results for pump B are very similar. 16-P-121 A: Hydraulic performance was performed acc. Inspection plan 6004 5656 step 2 with 5 points. KSB decided to run at least 9 points as follow (values from data sheet are mentioned in blue): A) 0 m3/h as shut off point with a head of 111.11 m (112.5 m), in tolerance of ±8%. B) 1480.6 m3/h (1480 m3/h) as min. allow. flow to check the stability of operation, C) 1752.9 m3/h as additional point to establish better curves, D) 2001.7 m3/h (1995 m3/h) as point between 95% and 99% of rated flow with a head of 94.85 m, E) 2120.2 m3/h (2205 m3/h) as point between 100% and 105% of rated flow with a head of 93.4 m (92 m), which is in tolerance of ±3%, F) 2298.4 m3/h as additional point, G) 2498.1 m3/h as additional point, H) 2749.5 m3/h as additional point, I) 3049.0 m3/h as max. point and best efficiency point. Measured power at rated point was 466.18 kW (465.1 kW), which is in tolerance of +4% rated efficiency was 83.04% (81.5 %), which is in tolerance of ±2.5&. Result was acceptable. NPSH test acc. to point 3 with five points: As NPSHa - NPSHr > 1 m, no NPSH test was required. Bearing temperature measurement acc. to ITP step 4: Bearing temperature was measured during the whole run test at outside of bearing bracket at drive end and pump end. Temperature was stable about 3 hours after start. Measured bearing temperatures were about 62.4 °C (motor side) and 57.5 °C (pump side) with a ambient temperature of 22.8°C. Temperature rise acc. to AN 1897/70-03/ AN 1897/70-09 is "ambient temperature + 50°K = 22.8°C + 50°K = 72.8°C". It means bearing temperature was acceptable. Please consider, that a temperature measurement of oil is not required acc. to ITP. |  |  |
| Sound test acc. to ITP step 5: Sound pressure level was measured at 1 m distance to the pump. Measured values was lightly higher than range of 85 dB(A) at 86,0 dB(A). Ambient noise was measured 81,0 dB(A). If we use a corrective factor o 3 or 4 dB(A), limit is not exceeded. Result was acceptable. Vibration Measurement ITP step 6: Vibration were measured on x, y and z direction by fitting of the sensors (magnet) at bearing bracket. Measured vibration unfiltered values Veff at rated flow vertical was 3.5 mm/s. This is in acceptable range of < 4.5 mm/s as mentioned on ITP and AN 1897/70-8 E rev. 00. Result was acceptable. Mechanical run test: Pump was connected via shop coupling to the shop motor. Vibration & temperature sensors on bearing brackets, flow meter at suction side, head measuring facility at discharge side, torque and rotation speed facility on shaft. Motor was started and run to the rated flow and rated head with constant speed and suction pressure of 1 barg. Pump was run for at least 240 min.. Result was acceptable. 16-P-122 A: Hydraulic performance was performed acc. Inspection plan 6004 5657 step 2 with 5 points. KSB decided to run at least 8 points as follow (values from data sheet are mentioned in blue): A) 0 m3/h as shut off point with a head of 99.74 m (99 m), in tolerance of ±8%. B) 1432.2 m3/h (1430 m3/h) as min. allow. flow to check the stability of operation, C) 1665.0 m3/h as additional point to establish better curves, D) 2001.7 m3/h (1995 m3/h) as point between 95% and 99% of rated flow with a head of 80.66 m, E) 2120.8 m3/h (2205 m3/h) as point between 100% and 105% of rated flow with a head of 78.47 m (76.93 m), which is in tolerance of +3%, F) 2376.9 m3/h as additional point, G) 2846.7 m3/h as best efficiency point, H) 2900.2 m3/h as max. point. Measured power at rated point was 393.03 kW (393.7 kW), which is in tolerance of +4% rated efficiency was 82.96% (80.5%). Result was acceptable. NPSH test acc. to point 3 with five points: As NPSHa - NPSHr = > 1 m, no NPSH test was required. Bearing temperature measurement acc. to ITP step 4: Bearing temperature was measured during the whole run test at outside of bearing bracket at drive end and pump end. Temperature was stable about 3 hours after start. Measured bearing temperatures were about 73.5 °C (motor side) and 66.4 °C (pump side) with a ambient temperature of 24.5°C. Temperature rise acc. to AN 1897/70-03/ AN 1897/70-09 is "ambient temperature + 50°K = 25.5°C + 50°K = 75.5°C". It means bearing temperature was acceptable. Please consider, that a temperature measurement of oil is not required acc. to ITP. |  |  |
| Sound test acc. to ITP step 5: Sound pressure level was measured at 1 m distance to the pump. Measured values was lightly higher than range of 85 dB(A) at 86,0 dB(A). Ambient noise was measured 81,0 dB(A). If we use a corrective factor o 3 or 4 dB(A), limit is not exceeded. Result was acceptable. Vibration Measurement ITP step 6: Vibration were measured on x, y and z direction by fitting of the sensors (magnet) at bearing bracket. Measured vibration unfiltered values Veff at rated flow axial was 3.4 mm/s. This is in acceptable range of < 4.5 mm/s as mentioned on ITP and AN 1897/70-8 E rev. 00. Result was acceptable. Mechanical run test: Pump was connected via shop coupling to the shop motor. Vibration & temperature sensors on bearing brackets, flow meter at suction side, head measuring facility at discharge side, torque and rotation speed facility on shaft. Motor was started and run to the rated flow and rated head with constant speed and suction pressure of 1 barg. Pump was run for at least 240 min.. Result was acceptable. Pump 16-P-122 B was made some unusual noises during the starting of mechanical run. Mechanical run was immediately stopped and pump was opened. As visible on attached photos, bearing was damaged in the pump. KSB is going to check all other pump pieces regarding damages and after installing new bearings, test must be repeated. Client will decide about it. 16-P-123 A: Hydraulic performance was performed acc. Inspection plan 6004 5658 step 2 with 5 points. KSB decided to run at least 9 points as follow (values from data sheet are mentioned in blue): A) 0 m3/h as shut off point with a head of 94.01 m (95.0 m), in tolerance of ±8%. B) 1409.5 m3/h (1408 m3/h) as min. allow. flow to check the stability of operation, C) 1615.2 m3/h as additional point to establish better curves, C) 1852.7 m3/h as additional point to establish better curves, D) 2001.9 m3/h (1995 m3/h) as point between 95% and 99% of rated flow with a head of 75.76 m, E) 2121.2 m3/h (2205 m3/h) as point between 100% and 105% of rated flow with a head of 73.55 m (71.93 m), which is in tolerance of ±3%, F) 2297.9 m3/h as additional point, G) 2769.1 m3/h and best efficiency point, H) 2861.1 m3/h as max. point. Measured power at rated point was 369.64 kW (368.2 kW), which is in tolerance of +4% rated efficiency was 82.63% (80.5 %), which is in tolerance of ±2.5&. Result was acceptable. Bearing temperature measurement acc. to ITP step 4: Bearing temperature was measured during the whole run test at outside of bearing bracket at drive end and pump end. Temperature was stable about 3 hours after start. Measured bearing temperatures were about 73.5 °C (motor side) and 53.2 °C (pump side) with a ambient temperature of 53.5°C. Temperature rise acc. to AN 1897/70-03/ AN 1897/70-09 is "ambient temperature + 50°K = 22.9°C + 50°K = 72.9°C". It means bearing temperature was acceptable. Please consider that a temperature measurement of oil is not required acc. to ITP. |  |  |
| Sound test acc. to ITP step 5: Sound pressure level was measured at 1 m distance to the pump. Measured values was lightly higher than range of 85 dB(A) at 86,0 dB(A). Ambient noise was measured 81,0 dB(A). If we use a corrective factor o 3 or 4 dB(A), limit is not exceeded. Result was acceptable. Vibration Measurement ITP step 6: Vibration were measured on x, y and z direction by fitting of the sensors (magnet) at bearing bracket. Measured vibration unfiltered values Veff at rated flow axial was 3.2 mm/s. This is in acceptable range of < 4.5 mm/s as mentioned on ITP and AN 1897/70-8 E rev. 00. Result was acceptable. Mechanical run test: Pump was connected via shop coupling to the shop motor. Vibration & temperature sensors on bearing brackets, flow meter at suction side, head measuring facility at discharge side, torque and rotation speed facility on shaft. Motor was started and run to the rated flow and rated head with constant speed and suction pressure of 1 barg. Pump was run for at least 240 min.. Result was acceptable. 16-P-131 A: Hydraulic performance was performed acc. Inspection plan 6004 5661 step 2 with 5 points. KSB decided to run at least 8 points as follow (values from data sheet are mentioned in blue): A) 0 m3/h as shut off point with a head of 122.18 m (118.00 m), in tolerance of ±10%. B) 251.92 m3/h (250 m3/h) as min. allow. flow to check the stability of operation, C) 426.87 m3/h as additional point to establish better curves, D) 577.85 m3/h (570 m3/h) as point between 95% and 99% of rated flow with a head of 111.81 m, E) 607.,35 m3/h (630 m3/h) as point between 100% and 105% of rated flow with a head of 112.51 m (108.7 m), which is in tolerance of +3%, F) 721.99 m3/h as additional point, G) 841.27 m3/h as best efficiency point, H) 972.74 m3/h as max. point. Measured power at rated point was 188.35 kW (182.6 kW), which is in tolerance of +4% rated efficiency was 73.82% (73%). Result was acceptable. Bearing temperature measurement acc. to ITP step 4: Bearing temperature was measured during the whole run test at outside of bearing bracket at drive end and pump end. Temperature was stable about 3 hours after start. Measured bearing temperatures were about 73.5 °C (motor side) and 62.0 °C (pump side) with a ambient temperature of 63.6°C. Temperature rise acc. to AN 1897/70-03/ AN 1897/70-09 is "ambient temperature + 50°K = 24°C + 50°K = 74°C". It means bearing temperature was acceptable. Please consider that a temperature measurement of oil is not required acc. to ITP. Sound test acc. to ITP step 5: Sound pressure level was measured at 1 m distance to the pump. Measured values was lightly higher than range of 85 dB(A) at 86,0 dB(A). Ambient noise was measured 81,0 dB(A). If we use a corrective factor o 3 or 4 dB(A), limit is not exceeded. |  |  |
| Vibration Measurement ITP step 6: Vibration were measured on x, y and z direction by fitting of the sensors (magnet) at bearing bracket. Measured vibration unfiltered values Veff at rated flow horizontal was 1.6 mm/s. This is in acceptable range of < 4.5 mm/s as mentioned on ITP and AN 1897/70-8 E rev. 00. Result was acceptable. Mechanical run test: Pump was connected via shop coupling to the shop motor. Vibration & temperature sensors on bearing brackets, flow meter at suction side, head measuring facility at discharge side, torque and rotation speed facility on shaft. Motor was started and run to the rated flow and rated head with constant speed and suction pressure of 1 barg. Pump was run for at least 240 min.. - Test result for pumps with tag numbers 16-P-121 A/B, 16-P-122 A, 16-P-123 A/B and 16-P-131 A/B was acceptable - Pump 16-P-122 B was made some unusual noises during the starting of mechanical run. Mechanical run was immediately stopped and pump was opened. As visible on attached photos, bearing was damaged in the pump. KSB is going to check all other pump pieces regarding damages and after installing new bearings, test must be repeated. Client will decide about it. Water analysis test report was reviewed with a chloride of 13 ppm, which is less than 50 ppm. Calibration certificates of test benches were reviewed and verified. Calibration date was not exceeded. 19-2) Instruments Used (Meter ,Slide Caliper ,Gauge,…) and Calibration Code/Date: Inspection was performed visually, so no instrument was used. Item; Instruments Used; Serial Number; Calibration Validity Date. |
| 20) Quantity Inspection (Detailed description of inspected quantity and assessment of quantity control): |  |
| Focus of inspection was performance test. Eight pumps were tested as requested. |  |
| 21) Packing Inspection (Detailed description of packing and suitability with the means of transport): |  |
| No packing inspection |  |
| 22) Shipping Mark Inspection (Detailed description of marking on the packages): |  |
| No shipping marking inspected. |  |
| 23) Loading / Stuffing Inspection: |  |
| Weather condition: |  |
| Start of loading time: | Finish of loading time: |
| No. of container(s): |  |
| Seal No.(s): |  |
| Comments on Loading / Stuffing Inspection: |  |
| Load was not part of inspection |  |
| 24) Discrepancies (Detailed description of discrepancies observed during inspection): |  |
| - Discrepancies which found during inspection and already obviated : |  |
| - Discrepancies which are still remained : |  |
| 1- Pump 16-P-122 B was made some unusual noises during the starting of mechanical run. Mechanical run was immediately stopped and pump was opened. As visible on attached photos, bearing was damaged in the pump. KSB is going to check all other pump pieces regarding damages and after installing new bearings, test must be repeated. 2- Performance test was performed according to API 610 and procedure AN1897/70-05 but mechanical run was performed acc. to AN1897/70-09 with limits for bearing vibration and temperature mentioned in attached ITP signed by inspector. |  |
| 25) Attachments (List of attached documents): |  |
| Test reports, signed ITP, Calibration certificates. |  |
| 26) Comments (Regarding inspection – if any): |  |
| 27) Photos (Photos taken at the time of inspection): |  |
| Inspector used his mobile device to make photos. Unfortunatley, there was some problems with internal drive of mobile, so almost all the photos and video clips are lost. Inspector could save only some photos as visible below. |  |

| 16-P-122 A under test | 16-P-122 A Performance points |
| --- | --- |
| 16-P-122 A Vibration and temperatures |  |
| 16-P-122 B Damaged bearing | 16-P-122 B Damaged bearing |
| 16-P-122 B Damaged bearing |  |
| 16-P-123 A performance points | 16-P-123 A Temperatures and vibration |