| 1) Inspector Name: Mohammad Ahmadi Inspector Code: 1617 Tel: +43 660 7325790 Email: |  | 2) Inspection Date: 08.07.2025 |  |  |  | 3) Project Name (if any): - |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 4) Scope of Inspection Required: Visual check, Quantity check, Packing & Marking, Review of documents Inspection Notification No.: - |  |  |  |  |  |  |  |
| 5) Inspection Address & Contact Info: Company Name: Adler Logistik GMBH Address: Concord Business Park 1, B6, 104, 2320 Schwechat, Austria Contact Name: Amir Khazanehdari Phone Number / Mobile Number: +436645584444 E-mail Address: |  |  |  |  |  |  |  |
| 6) Inspection Place: Manufacturer Supplier ☒ Warehouse Port Customs Others Specify: |  |  |  |  |  |  |  |
| 7) Client/Buyer: Aban Air Cooler |  |  |  | 8) Vendor/Sub-Vendor: CEMP / Fritech GmbH |  |  |  |
| 9) Goods as Per Purchasing Documents: 2 x LV motors, 3 Kw, IP55, 750 rpm, IMV6, 400VAC, 3Ph, 50Hz, Enclosure: EExd IIB T3, one per phase PTC in separated TB |  |  |  |  |  |  |  |
| 10) Quality Inspection : |  |  |  |  |  |  |  |
| ☒ Visual | Dimensional check |  | Test |  | ☒ Doc’s Review |  |  |
| ☒ %100 Spot Check | %100 Spot Check |  | %100 Spot Check |  |  |  |  |
| Random No. of Items Checked: | Random No. of Items Checked: |  | Random No. of Items Checked: |  |  |  |  |
| 11) Quantity Inspection : |  |  |  |  |  |  |  |
| Tally | Weight |  | Volume |  | Length |  | Others (Specify) |
| ☒ %100 Spot Check | %100 Spot Check |  | %100 Spot Check |  | %100 Spot Check |  |  |
| Random No. of Items Checked: 2 | Random No. of Items Checked: |  | Random No. of Items Checked: |  | Random No. of Items Checked: |  |  |
| 12) Brief Description of Packing: Kind of Packing: Wooden Box Total Number of Packages: 1 Total Net weight: KG Total Gross weight: KG |  |  | 13) Shipping Mark (Please specify details in item 22): Initial Shipping marks were available on the box. However, the Final Shipping mark was not available. |  |  |  |  |
| 14) Means of Transport: Truck Vessel Air Rail Combined Shipment From: Austria Via: Italy To: Tehran |  |  |  |  |  |  |  |
| 15) Conclusion (Explain Briefly): Stage (Inspection of the goods in this visit is satisfactory. Goods are released for further inspection) Satisfactory (Inspection of the goods is satisfactory. Goods are released for shipment) Non-Conformity (Discrepancies observed. Goods could not be released) Abortive (Due to missing goods and/or documents, inspection could not be carried out) Inspection completed? No Yes ☒ When No, Specify next insp. scope: |  |  |  |  |  |  |  |
| 16) Documents Used for Inspection: L/C No.: -; No. of L/C Amendments: -; P/I No.: -. Tech. Spec. No.: -; P/O No. / MR No.: 17222-El-5012-1; ITP No.: n/a. Drawing No.: -; Procedure No.:; Data Sheet No.: -. Others:. Necessary Documents for Issuance of COI Has Been Collected: Yes No ☒. |
| 17) Goods Inspected In Details: Model; Serial Number; Description; QTY. E3AB300B137B30D41100-11799347; 2500007312 2500007313; Electric Motors 3 Kw, IP55, 400VAC, 3Ph, 50Hz E3AB30 132MB 8 V6 3F 230D/400S/50 3,00; 2. |
| 18) Order Completed? Yes ☒ No Comments (If any): |  |  |  |  |  |  |  |

| 19) Quality Inspection (Detailed description of quality inspection and assessment of quality control): |  |  |  |  |
| --- | --- | --- | --- | --- |
| Visual inspection was carried out on two Electric motors, rated at 3 kW, IP55, 750 rpm, IMV6, 400VAC, 3Ph, 50Hz. The motors were free from visible damage, corrosion, or deformation. Surface finish, painting quality, and protective coatings were found acceptable. Nameplate details were legible and firmly affixed. However, two deviations from the Purchase Order (PO) specifications were noted: - Speed marking: Nameplate indicated 729 rpm instead of the specified 750 rpm. Vendor clarified that 729 rpm reflects the actual tested speed, supported by test reports. - Explosion proof marking: Nameplate indicated “Ex db IIB T4 Gc” whereas PO required “EExd IIB T3”. Although “T4” offers a safer temperature class and “Ex db” aligns with current IEC standards, the marking is technically different. This deviation requires validation against project specifications or confirmation from the end-user for compliance. Provided documents were reviewed and a summary is provided below: - EU-Type Examination Certificate issued by TÜV CYPRUS Ltd (TÜV NORD Group) for a range of flameproof three-phase asynchronous electrical motors and brake motors manufactured by CEMP S.r.l. in Italy. These motors are certified under Directive 2014/34/EU for use in potentially explosive atmospheres and comply with essential health and safety requirements per EN and IEC standards such as EN IEC 60079-0, EN 60079-1, and others. The certificate covers multiple motor types and configurations, detailing their protection methods (Ex db, Ex eb, Ex tb), sizes, efficiency classes (IE1 to IE4), cooling systems (IC410, IC411, IC416, IC418), optional accessories, and compatibility with inverter supplies. Special conditions for safe use, routine testing protocols—such as overpressure tests—and identification coding schemes are also specified, reflecting certification oversight and compliance with ATEX requirements. - The Type Test Report Nr. 2023 CE70047328-1-0 issued by CEMP, for a flameproof three-phase asynchronous motor (model: E3AB30 132MB 8 V6 230D / 400Y V 50Hz, 3kW). The report demonstrates compliance with IEC 60034-1 standards and outlines performance data across varying loads—from no-load to full-load and locked rotor conditions. Key parameters such as input/output power, current, efficiency, torque, and speed are recorded. The motor meets ATEX requirements for use in explosive atmospheres, rated Ex db IIB T4 Gb. Additional tests include insulation resistance, sound pressure level, vibration assessment, and temperature rise in copper windings and bearings. All results fall within acceptable tolerances, confirming mechanical integrity and safe operational characteristics under standard testing conditions. - The Routine Test Certificate Nr. 2025.CE70047328-1-0 issued by CEMP for flameproof asynchronous motors, confirming compliance with IEC 60034-1 standards. It summarizes acceptance tests performed on two motor units (serial numbers 2500007312 and 2500007313), including electrical checks like phase resistance, no-load current and power losses, starting current and torque measurements, as well as high-voltage and insulation resistance tests. Mechanical inspections—covering vibration, bearing noise, rotation direction, dimensional conformity, and visual finishing—were also successfully passed. All test items are marked as compliant (“X”), certifying the motors match their type-approved prototypes and are cleared for operational deployment in accordance with safety and performance standards. |  |  |  |  |
| 19-1) Marking on Goods as per specific requirements: |  |  |  |  |
| Various markings were observed on the items: - Warning labels and plates - Specifications - Main Nameplate Markings were cross-checked with the provided documents and verified. The deviation was mentioned in section 19. |  |  |  |  |
| 19-2) Instruments Used (Meter ,Slide Caliper ,Gauge,…) and Calibration Code/Date: |  |  |  |  |
| Item; Instruments Used; Serial Number; Calibration Validity Date. -; -; -; -. |
| 20) Quantity Inspection (Detailed description of inspected quantity and assessment of quantity control): |  |  |  |
| The quantity check verified the presence of two (2) Electric Motors as per the PO. Serial numbers were cross-checked against documentation. No discrepancies were noted in quantity. Items were new and matched the expected make and model. |  |  |  |
| 21) Packing Inspection (Detailed description of packing and suitability with the means of transport): |  |  |  |
| Packing inspection was performed on a single wooden box containing two (2) LV motors. The motors were securely fixed using two packing bandages to prevent any movement during transit. A carton separator was placed between the two units to avoid contact damage. One desiccant pouch was observed inside the box, serving as a moisture control measure. |  |  |  |
| 22) Shipping Mark Inspection (Detailed description of marking on the packages): |  |  |  |
| External packing featured standard shipping markings and handling instructions, including orientation arrows, applied by both the manufacturer and transportation company. A packing list was affixed to the outer surface of the box. However, the available markings during the inspection were those affixed by the original vendor, but there was no shipping marking indicating the information about the Final consignee, either in Tehran or Shiraz, Iran. |  |  |  |
| 23) Loading / Stuffing Inspection: |  |  |  |
| Weather condition: - |  |  |  |
| Start of loading time: - |  | Finish of loading time: |  |
| No. of container(s): - |  |  |  |
| Seal No.(s): - |  |  |  |
| Comments on Loading / Stuffing Inspection: |  |  |  |
| Not Applicable |  |  |  |
| 24) Discrepancies (Detailed description of discrepancies observed during inspection): |  |  |  |
| - Discrepancies which found during inspection and already obviated : |  |  |  |
| - Discrepancies which are still remained : |  |  |  |
| 1.Speed marking: Nameplate indicated 729 rpm instead of the specified 750 rpm. Vendor stated that 729 rpm reflects the actual tested speed, supported by test reports. 2.Explosion proof marking: Nameplate indicated “Ex db IIB T4 Gc” whereas PO required “EExd IIB T3”. Although “T4” offers a safer temperature class and “Ex db” aligns with current IEC standards, the marking is technically different. 3. The client’s approval on Packing manner (as explained in section 21 of inspection report) is needed, as no packing procedure received from the client. 4.Lack of facility to weigh the package. 5.Packing list was not ready. 6. The goods will be shipped to Marathon weg group according to Shipping mark. 7. The client’s approval on the inspection report is needed |  |  |  |
| 25) Attachments (List of attached documents): |  |  |  |
| Sr No.; Attachment name; Description; No. of pages. 1; E3_E4-TUV-CY-17-ATEX-0205845-X-Issue-12; EU-TYPE-Examination Certificate acc . to the Directive 2014/34/EU; 13. 2; PTTR; APPORTO DI COLLAUDO DEL PROTOTIPO - TYPE TEST REPORT Nr. 2023 CE70047328-1-0 Norme/Standards IEC 60034-1; 1. 3; RTC; PROVA DI ACCETTAZIONE / ROUTINE TEST N.ro / Nr. 2025.CE70047328-1-0; 1. |
| 26) Comments (Regarding inspection – if any): |  |  |  |
| None |  |  |  |
| 27) Photos (Photos taken at the time of inspection): |  |  |  |
| Photo No.1: Packing check |  | Photo No.2: Packing check |  |
| Photo No.3: Packing check |  | Photo No.4: Packing check |  |
| Photo No.5: Visual check |  | Photo No.6: Visual check |  |
| Photo No.7: Visual check |  | Photo No.8: Visual check |  |
| Photo No.9: Visual check |  | Photo No.10: Visual check |  |
| Photo No.11: Visual check |  | Photo No.12: Visual check |  |
| Photo No.13: Visual check / Label check |  | Photo No.14: Visual check / Label check |  |
| Photo No.15: Warning plate |  | Photo No.16: Warning plate |  |
| Photo No.17: Nameplate check |  | Photo No.18: Nameplate check |  |
| Photo No.19: Nameplate check |  | Photo No.20: Nameplate check |  |
| Photo No.21: Visual check |  | Photo No.22: Shipping marking check |  |
| Photo No.23: Shipping marking check |  | Photo No.24: Packing List attached |  |